## Sampling sequence
First draft of sampling sequence
|  | Ctrl State value = 1, pressure valve number, pump status, sampling valve number, Xbee query | [13 empty] | OFF mode | [9 empty] | ON mode (when burner starts)
|  | Ctrl State |  |  |  | Pressure valves |  |  |  |  | Sampling valves | [9 empty] | Execute occasionally (15 min) | [9 empty] | Execute occasionally (15 min)
| Second | Prior Ctrl Value | Prior Ctrl Value | New Ctrl Value | Meas Temps | 1 Zero | 2 Zone | 3 WH Vent | 4 Furn Vent | Samp Pump | 5 WH Vent | 6 Furn Vent | 7 Room Low | CO2 variable | Xbee | Second | Pressure valve | Valve change (after read) | Read data | Use data? | CO2 valve | Valve change (after read) | Pump | Read data | Use data? | Second of burner operation | Pressure valve | Valve change (after read) | Read data | Use data? | CO2 valve | Valve change (after read) | Pump | Read data | Use data?
| 1 | Test | 10000 | 11151 | Yes | Setup |  |  |  | ON | Setup |  |  | co2_wh | Initiate query | 57 | 3_whvent | 3 -> 4 | Scan x 25 |  | off |  | off | No | No | p | 4_fvent | 4 -> 1 | Scan x 25 |  | off |  | off | No | No
| 2 |  |  | 11150 | Yes | Scan x 25 |  |  |  | ON | Scan |  |  |  | Query running | 58 | 4_fvent |  | Scan x 25 | No ? | off |  | off | No | No | q | 1_zero |  | Scan x 25 | Setup delay? | off |  | off | No | No
| 3 |  |  | 11150 | Yes | Scan x 25 |  |  |  | ON | Scan |  |  |  | Query running | 59 | 4_fvent |  | Scan x 25 | Yes | off |  | off | No | No | r | 1_zero |  | Scan x 25 |  | off |  | off | No | No
| 4 |  |  | 12150 | Yes |  | Setup |  |  | ON | Scan |  |  |  | Query running | 60 | 4_fvent | 4 -> 1 | Scan x 25 | Yes | off | 5 on | ON | No | No | s | 1_zero | 1 -> 2 | Scan x 25 |  | off |  | off | No | No
| 5 |  |  | 12150 | Yes |  | Scan x 25 |  |  | ON | Scan |  |  |  | Query running | 1 | 1_zero |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay | t | 2_zone |  | Scan x 25 | Setup delay? | off |  | off | No | No
| 6 |  |  | 12150 | Yes |  | Scan x 25 |  |  | ON | Scan |  |  |  | Query running | 2 | 1_zero |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 1 | 2_zone |  | Scan x 25 |  | off | 5 on | ON | No | No
| 7 |  |  | 13150 | Yes |  |  | Setup |  | ON | Scan |  |  |  | Query running | 3 | 1_zero | 1 -> 2 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 2 | 2_zone | 2 -> 3 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | When burner starts, prior accumulated data is closed out and written to a record, and 1-sec data collection begins here
| 8 |  |  | 13150 | Yes |  |  | Scan x 25 |  | ON | Scan |  |  |  | Query running | 4 | 2_zone |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay | 3 | 3_whvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 9 |  |  | 13150 | Yes |  |  | Scan x 25 |  | ON | Scan |  |  |  | Query running | 5 | 2_zone |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 4 | 3_whvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 10 |  |  | 14150 | Yes |  |  |  | Setup | ON | Scan |  |  |  | (to completion or timeout) | 6 | 2_zone | 2 -> 3 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 5 | 3_whvent | 3 -> 4 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 11 |  |  | 14150 | Yes |  |  |  | Scan x 25 | ON | Scan |  |  |  |  | 7 | 3_whvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay | 6 | 4_fvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 12 |  |  | 14150 | Yes |  |  |  | Scan x 25 | ON | Scan |  |  |  |  | 8 | 3_whvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 7 | 4_fvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 13 |  |  | 11150 | Yes | Setup |  |  |  | ON | Scan |  |  |  |  | 9 | 3_whvent | 3 -> 4 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 8 | 4_fvent | 4 -> 1 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 14 |  |  | 11150 | Yes | Scan x 25 |  |  |  | ON | Scan |  |  |  |  | 10 | 4_fvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay | 9 | 1_zero |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 15 |  |  | 11150 | Yes | Scan x 25 |  |  |  | ON | Scan |  |  |  |  | 11 | 4_fvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 10 | 1_zero |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 16 |  |  | 12150 | Yes |  | Setup |  |  | ON | Scan |  |  |  |  | 12 | 4_fvent | 4 -> 1 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 11 | 1_zero | 1 -> 2 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 17 |  |  | 12150 | Yes |  | Scan x 25 |  |  | ON | Scan |  |  |  |  | 13 | 1_zero |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data | 12 | 2_zone |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 18 |  |  | 12150 | Yes |  | Scan x 25 |  |  | ON | Scan |  |  |  |  | 14 | 1_zero |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 13 | 2_zone |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 19 |  |  | 13150 | Yes |  |  | Setup |  | ON | Scan |  |  |  |  | 15 | 1_zero | 1 -> 2 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 14 | 2_zone | 2 -> 3 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 20 |  |  | 13150 | Yes |  |  | Scan x 25 |  | ON | Scan |  |  |  |  | 16 | 2_zone |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data | 15 | 3_whvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 21 |  |  | 13150 | Yes |  |  | Scan x 25 |  | ON | Scan |  |  |  |  | 17 | 2_zone |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 16 | 3_whvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 22 |  |  | 14150 | Yes |  |  |  | Setup | ON | Scan |  |  |  |  | 18 | 2_zone | 2 -> 3 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 17 | 3_whvent | 3 -> 4 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 23 |  |  | 14150 | Yes |  |  |  | Scan x 25 | ON | Scan |  |  |  |  | 19 | 3_whvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data | 18 | 4_fvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 24 |  |  | 14150 | Yes |  |  |  | Scan x 25 | ON | Scan |  |  |  |  | 20 | 3_whvent |  | Scan x 25 |  | 5_whvent | 5 -> 6 | ON | Yes | Use data | 19 | 4_fvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 25 |  |  | 11160 | Yes | Setup |  |  |  | ON |  | Setup |  |  |  | 21 | 3_whvent | 3 -> 4 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 20 | 4_fvent | 4 -> 1 | Scan x 25 |  | 5_whvent | 5 -> 6 | ON | Yes | Use data
| 26 |  |  | 11160 | Yes | Scan x 25 |  |  |  | ON |  | Scan |  |  |  | 22 | 4_fvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay | 21 | 1_zero |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay
| 27 |  |  | 11160 | Yes | Scan x 25 |  |  |  | ON |  | Scan |  |  |  | 23 | 4_fvent |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 22 | 1_zero |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 28 |  |  | 12160 | Yes |  | Setup |  |  | ON |  | Scan |  |  |  | 24 | 4_fvent | 4 -> 1 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 23 | 1_zero | 1 -> 2 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 29 |  |  | 12160 | Yes |  | Scan x 25 |  |  | ON |  | Scan |  |  |  | 25 | 1_zero |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay | 24 | 2_zone |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay
| 30 |  |  | 12160 | Yes |  | Scan x 25 |  |  | ON |  | Scan |  |  |  | 26 | 1_zero |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 25 | 2_zone |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 31 |  |  | 13160 | Yes |  |  | Setup |  | ON |  | Scan |  |  |  | 27 | 1_zero | 1 -> 2 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 26 | 2_zone | 2 -> 3 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 32 |  |  | 13160 | Yes |  |  | Scan x 25 |  | ON |  | Scan |  |  |  | 28 | 2_zone |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay | 27 | 3_whvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay
| 33 |  |  | 13160 | Yes |  |  | Scan x 25 |  | ON |  | Scan |  |  |  | 29 | 2_zone |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 28 | 3_whvent |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 34 |  |  | 14160 | Yes |  |  |  | Setup | ON |  | Scan |  |  |  | 30 | 2_zone | 2 -> 3 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 29 | 3_whvent | 3 -> 4 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 35 |  |  | 14160 | Yes |  |  |  | Scan x 25 | ON |  | Scan |  |  |  | 31 | 3_whvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data | 30 | 4_fvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay
| 36 |  |  | 14160 | Yes |  |  |  | Scan x 25 | ON |  | Scan |  |  |  | 32 | 3_whvent |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 31 | 4_fvent |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 37 |  |  | 11160 | Yes | Setup |  |  |  | ON |  | Scan |  |  |  | 33 | 3_whvent | 3 -> 4 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 32 | 4_fvent | 4 -> 1 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 38 |  |  | 11160 | Yes | Scan x 25 |  |  |  | ON |  | Scan |  |  |  | 34 | 4_fvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data | 33 | 1_zero |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data
| 39 |  |  | 11160 | Yes | Scan x 25 |  |  |  | ON |  | Scan |  |  |  | 35 | 4_fvent |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 34 | 1_zero |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 40 |  |  | 12160 | Yes |  | Setup |  |  | ON |  | Scan |  |  |  | 36 | 4_fvent | 4 -> 1 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 35 | 1_zero | 1 -> 2 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 41 |  |  | 12160 | Yes |  | Scan x 25 |  |  | ON |  | Scan |  |  |  | 37 | 1_zero |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data | 36 | 2_zone |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data
| 42 |  |  | 12160 | Yes |  | Scan x 25 |  |  | ON |  | Scan |  |  |  | 38 | 1_zero |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 37 | 2_zone |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 43 |  |  | 13160 | Yes |  |  | Setup |  | ON |  | Scan |  |  |  | 39 | 1_zero | 1 -> 2 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 38 | 2_zone | 2 -> 3 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 44 |  |  | 13160 | Yes |  |  | Scan x 25 |  | ON |  | Scan |  |  |  | 40 | 2_zone |  | Scan x 25 | Setup delay? | 6_fvent | 6 -> 7 | ON | Yes | Use data | 39 | 3_whvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data
| 45 |  |  | 13160 | Yes |  |  | Scan x 25 |  | ON |  | Scan |  |  |  | 41 | 2_zone |  | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 40 | 3_whvent |  | Scan x 25 |  | 6_fvent | 6 -> 7 | ON | Yes | Use data
| 46 |  |  | 14160 | Yes |  |  |  | Setup | ON |  | Scan |  |  |  | 42 | 2_zone | 2 -> 3 | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 41 | 3_whvent | 3 -> 4 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 47 |  |  | 14160 | Yes |  |  |  | Scan x 25 | ON |  | Scan |  |  |  | 43 | 3_whvent |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes? | Setup delay | 42 | 4_fvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 48 |  |  | 14160 | Yes |  |  |  | Scan x 25 | ON |  | Scan |  |  |  | 44 | 3_whvent |  | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 43 | 4_fvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 49 |  |  | 11170 | Yes | Setup |  |  |  | ON |  |  | Setup |  |  | 45 | 3_whvent | 3 -> 4 | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 44 | 4_fvent | 4 -> 1 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 50 |  |  | 11170 | Yes | Scan x 25 |  |  |  | ON |  |  | Scan |  |  | 46 | 4_fvent |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes? | Setup delay | 45 | 1_zero |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 51 |  |  | 11170 | Yes | Scan x 25 |  |  |  | ON |  |  | Scan |  |  | 47 | 4_fvent |  | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 46 | 1_zero |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 52 |  |  | 12170 | Yes |  | Setup |  |  | ON |  |  | Scan |  |  | 48 | 4_fvent | 4 -> 1 | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 47 | 1_zero | 1 -> 2 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 53 |  |  | 12170 | Yes |  | Scan x 25 |  |  | ON |  |  | Scan |  |  | 49 | 1_zero |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes? | Setup delay | 48 | 2_zone |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 54 |  |  | 12170 | Yes |  | Scan x 25 |  |  | ON |  |  | Scan |  |  | 50 | 1_zero |  | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 49 | 2_zone |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 55 |  |  | 13170 | Yes |  |  | Setup |  | ON |  |  | Scan |  |  | 51 | 1_zero | 1 -> 2 | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 50 | 2_zone | 2 -> 3 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 56 |  |  | 13170 | Yes |  |  | Scan x 25 |  | ON |  |  | Scan |  |  | 52 | 2_zone |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes | Use data | 51 | 3_whvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 57 |  |  | 13170 | Yes |  |  | Scan x 25 |  | ON |  |  | Scan |  |  | 53 | 2_zone |  | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 52 | 3_whvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 58 |  |  | 14170 | Yes |  |  |  | Setup | ON |  |  | Scan |  |  | 54 | 2_zone | 2 -> 3 | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 53 | 3_whvent | 3 -> 4 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 59 |  |  | 14170 | Yes |  |  |  | Scan x 25 | ON |  |  | Scan |  |  | 55 | 3_whvent |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes | Use data | 54 | 4_fvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 60 |  |  | 14170 | Yes |  |  |  | Scan x 25 | ON |  |  | Scan |  |  | 56 | 3_whvent |  | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 55 | 4_fvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 61 |  |  | 11170 | Yes | Setup |  |  |  | ON |  |  | Scan |  |  | 57 | 3_whvent | 3 -> 4 | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 56 | 4_fvent | 4 -> 1 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 62 |  |  | 11170 | Yes | Scan x 25 |  |  |  | ON |  |  | Scan |  |  | 58 | 4_fvent |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes | Use data | 57 | 1_zero |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 63 |  |  | 11170 | Yes | Scan x 25 |  |  |  | ON |  |  | Scan |  |  | 59 | 4_fvent |  | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 58 | 1_zero |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 64 |  |  | 12170 | Yes |  | Setup |  |  | ON |  |  | Scan |  |  | 60 | 4_fvent | 4 -> 1 | Scan x 25 |  | 7_room | off | off | Yes | Use data | 59 | 1_zero | 1 -> 2 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 65 |  |  | 12170 | Yes |  | Scan x 25 |  |  | ON |  |  | Scan |  |  | 1 | 1_zero |  | Scan x 25 | Setup delay? | off |  | off | No | No | 60 | 2_zone |  | Scan x 25 | Setup delay? | 7_room | off | off | Yes | Use data
| 66 |  |  | 12170 | Yes |  | Scan x 25 |  |  | ON |  |  | Scan |  |  | 2 | 1_zero |  | Scan x 25 |  | off |  | off | No | No | 1 | 2_zone |  | Scan x 25 |  | off |  | off | No | No
| 67 |  |  | 13170 | Yes |  |  | Setup |  | ON |  |  | Scan |  |  | 3 | 1_zero | 1 -> 2 | Scan x 25 |  | off |  | off | No | No | 2 | 2_zone | 2 -> 3 | Scan x 25 |  | off |  | off | No | No
| 68 |  |  | 13170 | Yes |  |  | Scan x 25 |  | ON |  |  | Scan |  |  | 4 | 2_zone |  | Scan x 25 | Setup delay? | off |  | off | No | No | 3 | 3_whvent |  | Scan x 25 | Setup delay? | off |  | off | No | No
| 69 |  |  | 13170 | Yes |  |  | Scan x 25 |  | ON |  |  | Scan |  |  |  | Repeat except CO2 samplng performed only occasionally | [8 empty] | 4 | 3_whvent |  | Scan x 25 |  | off |  | off | No | No
| 70 |  |  | 14170 | Yes |  |  |  | Setup | ON |  |  | Scan
| 71 |  |  | 14170 | Yes |  |  |  | Scan x 25 | ON |  |  | Scan
| 72 |  |  | 14170 | Yes |  |  |  | Scan x 25 | ON |  |  | Scan
| 73 |  |  | 10000 | Yes |  |  |  |  | OFF
| 74 |  |  | 10000 | Yes |  |  |  |  | OFF
| 75 |  |  | 10000 | Yes |  |  |  |  | OFF
| 76 |  |  | 10000 | Yes |  |  |  |  | OFF
| 77 |  |  | 10000 | Yes |  |  |  |  | OFF
| 78 |  |  | 10000 | Yes |  |  |  |  | OFF
| 79 |  |  | 10000 | Yes |  |  |  |  | OFF
| 80 |  |  | 10000 | Yes |  |  |  |  | OFF
| 81 |  |  | 10000 | Yes |  |  |  |  | OFF
| 82 |  |  | 10000 | Yes |  |  |  |  | OFF
| 83 |  |  | 10000 | Yes |  |  |  |  | OFF
| 84 |  |  | 10000 | Yes |  |  |  |  | OFF
| 85 |  |  | 10000 | Yes |  |  |  |  | OFF
| 86 |  |  | 10000 | Yes |  |  |  |  | OFF
| 87 |  |  | 10000 | Yes |  |  |  |  | OFF
| 88 |  |  | 10000 | Yes |  |  |  |  | OFF
| 89 |  |  | 10000 | Yes |  |  |  |  | OFF
| 90 |  |  | 10000 | Yes |  |  |  |  | OFF
Note on AK12: Actually want to start on the vent of the operating appliance.

## HardwareMapping
Notes
Board label | Connector designation | Amp | ADC | ADC mux # | I2C Address | BBB pins | BBB name | Connected device | Possible data parameter name (coordinate with object names)
TC1 | J20 1-2 | U17 | U11 | 0 | x | P9-17 (I2C1_SCL) P9-18 (I2C1_SDA) | I2C1 | WH burner temp | .whburner
TC2 | J20 3-4 | U16 | U11 | 1 |  | " | " | WH spill temp 1 | .whspill_1
TC3 | J20 5-6 | U18 | U11 | 2 |  | " | " | WH spill temp 2 | .whspill_2
TC4 | J20 7-8 | U19 | U11 | 3 |  | " | " | WH spill temp 3 | .whspill_3
TC5 | J20 9-10 | U20 | U13 | 0 | x | " | I2C1 | WH spill temp 4 | .whspill_4
TC6 | J20 11-12 | U21 | U13 | 1 |  | " | " | WH downstream vent temp | .whvent
TC7 | J21 1-2 | U22 | U13 | 2 |  | " | " | Furnace burner temp | .fburner
TC8 | J21 3-4 | U23 | U13 | 3 |  | " | " | Furnace spill temp 1 | .fspill_1
TC9 | J21 5-6 | U24 | U14 | 0 | x | " | I2C1 | Furnace spill temp 2 | .fspill_2
TC10 | J21 7-8 | U25 | U14 | 1 |  | " | " | Furnace spill temp 3 | .fspill_3
TC11 | J21 9-10 | U26 | U14 | 2 |  | " | " | Furnace spill temp 4 | .fspill_4
TC12 | J21 11-12 | U27 | U14 | 3 |  | " | " | Furnace downstream vent temp | .fvent
TC13 | J10 1-2 | U28 | U15 | 0 | x | " | I2C1 | Zone high temp | .zonehi
TC14 | J10 4-5 | U29 | U15 | 1 |  | " | " | Zone low temp | .zonelow
TC15 | J10 6-7 | U30 | U15 | 2 |  | " | " | Outdoor temp | .outdoor | TC amps U30 and U31 include voltage offset to allow reading temps < 32F
| J10 9-10 | U31 | U15 | 3 |  | " | " | Not used
[5 empty] | x | " | I2C1 | Pressure DLVR | [multiple] | Multiple data parameters, tied to valve position.
[5 empty] | x | " | I2C1 | RTC
JP1-A | J9-2 | na | U8 | 0 | x | P9-19 (I2C2_SCL) P9-20 (I2C2_SDA) | I2C2 | Door position | .door_1
JP1-B | J9-4 | na | U8 | 1 |  | " | " | Fan current 1 | .fan_1
JP1-C | J9-6 | na | U8 | 2 |  | " | " | Fan current 2 | .fan_2
JP1-D | J9-8 | U3 | U8 | 3 |  | " | " | Carbon monoxide | .cozone
ADC-6 | J25-1 | na | U9 | 0 | x | " | I2C2 | Carbon dioxide | [multiple] | Can put on any U9 or U10 input. Multiple data parameters, tied to valve position.
| J25-2 | na | U9 | 1 |  | " | " | Not used
| J25-3 | na | U9 | 2 |  | " | " | Not used
| J25-4 | na | U9 | 3 |  | " | " | Not used
ADC-7 | J25-5 | na | U10 | 0 | x | " | I2C2 | Not used
| J25-6 | na | U10 | 1 |  | " | " | Not used
| J25-7 | na | U10 | 2 |  | " | " | Not used
| J25-8 | na | U10 | 3 |  | " | " | Not used
[6 empty] | P9-11 | UART4_RXD | Xbee Dout (pin 2)
[6 empty] | P9-13 | UART4_TXD | Xbee Din (pin 3)
[6 empty] | P8-7 |  | Valve 1 zero pressure
[6 empty] | P8-8 |  | Valve 2 WH vent pressure
[6 empty] | P8-9 |  | Valve 3 Furnace vent pressure
[6 empty] | P8-10 |  | Valve 4 Zone pressure
[6 empty] | P8-11 |  | Valve 5 CO2 WH
[6 empty] | P8-12 |  | Valve 6 CO2 Furnace
[6 empty] | P8-13 |  | Valve 7 CO2 Zone
[6 empty] | P8-14 |  | Pump |  | Pump must be on P8-14 since it switches 3.3 V power
[6 empty] | P8-15 |  | Controls 24V power |  | Actively switched by BBB to avoid damage to inputs
[6 empty] | P8-16 |  | Switch_1 |  | Pushbutton switch - may use to start 1-sec data collection in setup/testing
[6 empty] | P8-17 |  | Switch_2 |  | No function designated

## DataParameters
Note when multiple summary values are collected in 60-sec scan (e.g. avg, min, max), each needs to have a separate field in data record
|  | 1-sec records | Longer records (1 minute) |  |  |  |  | 1-sec test mode | Diagnostics | Data Units/Format | Notes
Sensor or I/O device description | Name (coordinate with object names) | Sample | Avg _avg | Min _min | Max _max | Count _cnt | Other
Site ID |  | x |  |  |  |  | 1st | x |  | Alphanumeric | Derived from EEPROM Serial Number
Timestamp | time | x |  |  |  |  | 1st | x | 1st | UTC
Record number |  | x |  |  |  |  | assigned | x | assigned | Integer | Start from 1 on any re-boot
WH burner temp | .whburner | x | x | x | x |  |  | x |  | deg. F
WH spill temp 1 | .whspill_1 | x | x | x | x |  |  | x |  | deg. F
WH spill temp 2 | .whspill_2 | x | x | x | x |  |  | x |  | deg. F
WH spill temp 3 | .whspill_3 | x | x | x | x |  |  | x |  | deg. F
WH spill temp 4 | .whspill_4 | x | x | x | x |  |  | x |  | deg. F
WH downstream vent temp | .whvent | x | x | x | x |  |  | x |  | deg. F
Furnace burner temp | .fburner | x | x | x | x |  |  | x |  | deg. F
Furnace spill temp 1 | .fspill_1 | x | x | x | x |  |  | x |  | deg. F
Furnace spill temp 2 | .fspill_2 | x | x | x | x |  |  | x |  | deg. F
Furnace spill temp 3 | .fspill_3 | x | x | x | x |  |  | x |  | deg. F
Furnace spill temp 4 | .fspill_4 | x | x | x | x |  |  | x |  | deg. F
Furnace downstream vent temp | .fvent | x | x | x | x |  |  | x |  | deg. F
Zone high temp | .zonehi | x | x | x | x |  |  | x |  | deg. F
Zone low temp | .zonelow | x | x | x | x |  |  | x |  | deg.F
Outdoor temp | .outdoor | x | x | x | x |  |  | x |  | deg. F | TC amps U30 and U31 include voltage offset to allow reading temps < 32F
Door position | .door_1 | x | x | x | x |  |  | x |  | Bool. | Door Open, True?
Fan current 1 | .fan_1 | x | x | x | x |  |  | x |  | Amps
Fan current 2 | .fan_2 | x | x | x | x |  |  | x |  | Amps
Carbon monoxide | .cozone | x | x | x | x |  |  | x
CO2 location (valve) ID |  | x |  |  |  |  | 1st | x |  |  | Record values by location ID, i.e. put each measurement in a separate parameter (see next few lines). Recording current ID in detailed data collection is a check on this.
CO2 valve time on |  | x | ? |  |  |  |  | x |  |  | Number of seconds the current valve has been open - use to screen out data before settling time has passed
CO2 WH vent | .wh | x | x | x | x |  |  | x |  |  | Record always in 1-sec data collection, use if current (i.e. settling time has passed) in 60-sec record periods.
CO2 F vent | .f | x | x | x | x |  |  | x |  |  | same
CO2 Zone | .zone | x | x | x | x |  |  | x |  |  | same
Pressure location (valve) ID |  | x | [5 empty] | x |  |  | Record values by location ID, i.e. put each pressure measurement in a separate parameter (see next few lines). Recording current ID in detailed data collection is a check on this.
Pressure valve time on |  | x | [5 empty] | x |  |  | Number of seconds the valve has been open - use to screen out data before settling time has passed
Pressure zero - avg in scan | .zero | x | x | x | x |  | std dev | x |  |  | Record always in 1-sec data collection, use if current (i.e. settling time has passed) in 60-sec record periods. Average value within each scan.
Pressure zero - range in scan | .zerorange | x |  | x | x |  | ? | x |  |  | Range is max - min within a scan
Pressure wh vent - avg in scan | .whvent | x | x | x | x |  | std dev | x |  |  | Subtract current zero offset
Pressure wh vent - range in scan | .whventrange | x |  | x | x |  | ? | x
Pressure f vent - avg in scan | .fvent | x | x | x | x |  | std dev | x |  |  | Subtract current zero offset
Pressure f vent - range in scan | .fventrange | x |  | x | x |  | ? | x
Pressure zone - avg in scan | .zone | x | x | x | x |  | std dev | x |  |  | Subtract current zero offset
Pressure zone - range in scan | .zonerange | x |  | x | x |  | ? | x
wh burner status |  | x | x |  |  | x
f burner status |  | x | x |  |  | x
wh mode
f mode
system state
number_of_scans | [10 empty] | Number of scans represented in record (usually 1 or 60)
wh burner run time from burner start | time.whburnerrun | x |  |  |  |  | Sum |  |  |  | Record starting with a burner start, accumulate seconds of operation to burner stop (then accumulate seconds into cooldown, below)
f burner run time from burner start | time.fburnerrun | x |  |  |  |  | Sum |  |  |  | Similar to wh
wh cooldown time |  | x |  |  |  |  | Sum |  |  |  | Record starting with a burner stop, accumulate seconds of operation to end of cooldown period
f cooldown time |  | x |  |  |  |  | Sum |  |  |  | Similar to wh
Count of 1-second values in record |  | x |  |  |  | x |  | x |  |  | This is the divisor use to calculate averages over the record period.
Xbee A value 1 | xb_ | x |  |  |  |  | Sample | x |  |  | Xbee data, if present. Include individual samples in record, no averaging. Allow for up to 7 individual values during a 60-sec record period, i.e. 10 sec sampling interval with some error.
Xbee A value 2 | xb_ | x |  |  |  |  | Sample | x
Xbee A value 3 | xb_ | x |  |  |  |  | Sample | x
Etc
Xbee B value 1 … | [10 empty] | Allow for up to 4 Xbees: A, B, C, D
Xbee C value 1 …
Xbee D value 1 …
Accumulated pump run time (hrs) | [8 empty] | x
errors |  | x |  |  |  | x | Sum? | x |  |  | Sum of binary bit error values set in wh and furnace mode routines. Don't expect multiple errors to occur duinrg 60-sec record periods.

## BBB_Mapping
Equipment Specifications: |  |  | Requirements
Component | Attribute/Description | Reference Designator | Units | Min | Nominal | Maximum | Notes | Purpose | Map to BBB Pin/Input/Resource
Water Heater Central Monitor | Performance - capable of 1 second data scans |  | sec/scan | 0.5 sec | 1 sec | 5 sec | May drop into fast scan mode during an "event", typically lasting about 2 minutes (fire-up of gas hotwater heater)
| uSD Card Storage - capable of storing 6 months of approx. 1-second data |  | Y/N | Yes | Yes | Yes
| Remote Upgrades/Service possible |  | Y/N | No | Yes | Yes
| Can run custom programs |  | Y/N | Yes | Yes | Yes
| Restarts operation if UPS fails |  | Y/N | No | No | Yes
| Realtime Clock | [5 empty] | Exists onboard and is "Accurate" (or sync's with NTP server)
T01 | Analog Input 1 | AI01 | bit-resolution | 12-bit | 14-bit | 16-bit |  | AI's are off board, see Hi-Resolution Analog Input | I2C_SCL – P9_19, I2C_SDA – P9_20
T02 | Analog Input 2 | AI02 | bit-resolution | 12-bit | 14-bit | 16-bit
T03 | Analog Input 3 | AI03 | bit-resolution | 12-bit | 14-bit | 16-bit
T04 | Analog Input 4 | AI04 | bit-resolution | 12-bit | 14-bit | 16-bit
T05 | Analog Input 5 | AI05 | bit-resolution | 12-bit | 14-bit | 16-bit
T06 | Analog Input 6 | AI06 | bit-resolution | 12-bit | 14-bit | 16-bit
T07 | Analog Input 7 | AI07 | bit-resolution | 12-bit | 14-bit | 16-bit
T08 | Analog Input 8 | AI08 | bit-resolution | 12-bit | 14-bit | 16-bit
T09 | Analog Input 9 | AI09 | bit-resolution | 12-bit | 14-bit | 16-bit
DP01 | Analog Input 10 | AI10 | bit-resolution | 12-bit | 14-bit | 16-bit |  | All-Sensors Differential Pressure | I2C_SCL – P9_19, I2C_SDA – P9_20
| Digital Input 1 | DI01
| Digital Input 2 | DI02
| Digital Input 3 | DI03
| Digital Input 4 | DI04
| Digital Input 5 | DI05
| Digital Input 6 | DI06
| Digital Input 7 | DI07
| Digital Input 8 | DI08
PM01 | Digital Output 1 | DO01 |  |  |  |  | Off -- dP Internal Vent; On -- dP CAZ
PM02 | Digital Output 2 | DO02 |  |  |  |  | Off -- Floor Air (PIPE01); On -- above draft hood Air (PIPE02)
PUMP01 | Digital Output 3 | DO03 |  |  |  |  | Off -- no air sample; On -- Pass Air Sample over sensor
Possibly AM01, routing to AD01 | Digital Output 4 | DO04
Possibly AM01, routing to AD01 | Digital Output 5 | DO05
Possibly AM01, routing to AD01 | Digital Output 6 | DO06
| Digital Output 7 | DO07
| Digital Output 8 | DO08
AD01 | UART 1/Serial 1 | Ser01 | [5 empty] | Digi Xbee radio | UART4, P8_35, P8_33, P9_11, P9_13
| UART 2/Serial 2 | Ser02
| Communications Link | Eth01 |  |  |  |  | wired Ethernet Link (or wireless?)
Hi-Resolution Analog Input | 8-input, 16-bit ADC, Serial Interface | AD01 | bit-resolution | 16-bit | 16-bit | 16-bit | If external, high resolution… | ADS-1115's (up to 4SE, x4) | I2C_SCL – P9_19, I2C_SDA – P9_20
Analog Mux? | To switch between input temperature sensors? | AM01 | 4-ch | 4-ch | 8-ch |  | Only required if there's a shortage of high bit-resolution inputs
Pneumatic Mux? | To switch between pressure sensors? | PM01 | I.D., In. |  | 1/8"
Pneumatic Mux? | To Switch between CO2 inputs | PM02 | I.D., In. |  | 1/8"
Air Pump | To turn on CO2 sampling | PUMP01 | I.D., In. |  | 1/8"
Temperature Sensor Array - Above Draft Hood | Mounted axially around draft hood, approx 6? sensors | T01-T06?
Temperature Sensor - Near WH Burner | High Temp Thermocouple | T07
Temperature Sensor - Indoor air temp |  | T08
Temperature Sensor - Outdoor air temp |  | T09
Carbon Dioxide Sensor | Air sampling sensor | CO2-1
Carbon Dioxide Sensor Piping - near floor |  | PIPE01 | I.D., In. |  | 1/8"
Carbon Dioxide Sensor Piping - above draft hood |  | PIPE02 | I.D., In. |  | 1/8"
Differential Pressure Sensor | gas, 2-input differential pressure sensor | DP01
Internal Vent air sample piping | for performing dP in relation to indoor air (typically negative when operating) | PIPE03
Outdoor air sample Piping | for performing dP in relation to indoor air (typically negative during spillage event) | PIPE04
Indoor air sample Piping (w/in combustion appliance zone (CAZ)) | for performing differential pressure measurements | PIPE05
Remote Fan Sensor #1 - Clothes Dryer Fan | Current Switch Digital Input
Non-Volatile Data Storage
Wi-Fi Linked
Realtime Clock
Battery Operated
Remote Fan Sensor #2 - Bathroom Fan | Current Switch Digital Input
Non-Volatile Data Storage
Wi-Fi Linked
Realtime Clock
Battery Operated
Remote Fan Sensor #3 - Rangehood Fan | Current Switch Digital Input
Non-Volatile Data Storage
Wi-Fi Linked
Realtime Clock
Battery Operated
Wireless Router (connected to External Gateway)
External Gateway | Assumed to be available via Homeowner?
Uninterruptible Power Supply | power strip | UPS01
Power Supply for WH Central Monitor
Power Supply for CO2 Sensor
Power Supply for Air Pump
Power Supply for External Gateway
SDCard
Ethernet Cabling