## Sampling sequence
First draft of sampling sequence
|  | Ctrl State value = 1, pressure valve number, pump status, sampling valve number, Xbee query | [13 empty] | OFF mode | [9 empty] | ON mode (when burner starts)
|  | Ctrl State |  |  |  | Pressure valves |  |  |  |  | Sampling valves | [9 empty] | Execute occasionally (15 min) | [9 empty] | Execute occasionally (15 min)
| Second | Prior Ctrl Value | Prior Ctrl Value | New Ctrl Value | Meas Temps | 1 Zero | 2 Zone | 3 WH Vent | 4 Furn Vent | Samp Pump | 5 WH Vent | 6 Furn Vent | 7 Room Low | CO2 variable | Xbee | Second | Pressure valve | Valve change (after read) | Read data | Use data? | CO2 valve | Valve change (after read) | Pump | Read data | Use data? | Second of burner operation | Pressure valve | Valve change (after read) | Read data | Use data? | CO2 valve | Valve change (after read) | Pump | Read data | Use data?
| 1 | Test | 10000 | 11151 | Yes | Setup |  |  |  | ON | Setup |  |  | co2_wh | Initiate query | 57 | 3_whvent | 3 -> 4 | Scan x 25 |  | off |  | off | No | No | p | 4_fvent | 4 -> 1 | Scan x 25 |  | off |  | off | No | No
| 2 |  |  | 11150 | Yes | Scan x 25 |  |  |  | ON | Scan |  |  |  | Query running | 58 | 4_fvent |  | Scan x 25 | No ? | off |  | off | No | No | q | 1_zero |  | Scan x 25 | Setup delay? | off |  | off | No | No
| 3 |  |  | 11150 | Yes | Scan x 25 |  |  |  | ON | Scan |  |  |  | Query running | 59 | 4_fvent |  | Scan x 25 | Yes | off |  | off | No | No | r | 1_zero |  | Scan x 25 |  | off |  | off | No | No
| 4 |  |  | 12150 | Yes |  | Setup |  |  | ON | Scan |  |  |  | Query running | 60 | 4_fvent | 4 -> 1 | Scan x 25 | Yes | off | 5 on | ON | No | No | s | 1_zero | 1 -> 2 | Scan x 25 |  | off |  | off | No | No
| 5 |  |  | 12150 | Yes |  | Scan x 25 |  |  | ON | Scan |  |  |  | Query running | 1 | 1_zero |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay | t | 2_zone |  | Scan x 25 | Setup delay? | off |  | off | No | No
| 6 |  |  | 12150 | Yes |  | Scan x 25 |  |  | ON | Scan |  |  |  | Query running | 2 | 1_zero |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 1 | 2_zone |  | Scan x 25 |  | off | 5 on | ON | No | No
| 7 |  |  | 13150 | Yes |  |  | Setup |  | ON | Scan |  |  |  | Query running | 3 | 1_zero | 1 -> 2 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 2 | 2_zone | 2 -> 3 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | When burner starts, prior accumulated data is closed out and written to a record, and 1-sec data collection begins here
| 8 |  |  | 13150 | Yes |  |  | Scan x 25 |  | ON | Scan |  |  |  | Query running | 4 | 2_zone |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay | 3 | 3_whvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 9 |  |  | 13150 | Yes |  |  | Scan x 25 |  | ON | Scan |  |  |  | Query running | 5 | 2_zone |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 4 | 3_whvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 10 |  |  | 14150 | Yes |  |  |  | Setup | ON | Scan |  |  |  | (to completion or timeout) | 6 | 2_zone | 2 -> 3 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 5 | 3_whvent | 3 -> 4 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 11 |  |  | 14150 | Yes |  |  |  | Scan x 25 | ON | Scan |  |  |  |  | 7 | 3_whvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay | 6 | 4_fvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 12 |  |  | 14150 | Yes |  |  |  | Scan x 25 | ON | Scan |  |  |  |  | 8 | 3_whvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 7 | 4_fvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 13 |  |  | 11150 | Yes | Setup |  |  |  | ON | Scan |  |  |  |  | 9 | 3_whvent | 3 -> 4 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay | 8 | 4_fvent | 4 -> 1 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 14 |  |  | 11150 | Yes | Scan x 25 |  |  |  | ON | Scan |  |  |  |  | 10 | 4_fvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay | 9 | 1_zero |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 15 |  |  | 11150 | Yes | Scan x 25 |  |  |  | ON | Scan |  |  |  |  | 11 | 4_fvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 10 | 1_zero |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 16 |  |  | 12150 | Yes |  | Setup |  |  | ON | Scan |  |  |  |  | 12 | 4_fvent | 4 -> 1 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 11 | 1_zero | 1 -> 2 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 17 |  |  | 12150 | Yes |  | Scan x 25 |  |  | ON | Scan |  |  |  |  | 13 | 1_zero |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data | 12 | 2_zone |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 18 |  |  | 12150 | Yes |  | Scan x 25 |  |  | ON | Scan |  |  |  |  | 14 | 1_zero |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 13 | 2_zone |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 19 |  |  | 13150 | Yes |  |  | Setup |  | ON | Scan |  |  |  |  | 15 | 1_zero | 1 -> 2 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 14 | 2_zone | 2 -> 3 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 20 |  |  | 13150 | Yes |  |  | Scan x 25 |  | ON | Scan |  |  |  |  | 16 | 2_zone |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data | 15 | 3_whvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 21 |  |  | 13150 | Yes |  |  | Scan x 25 |  | ON | Scan |  |  |  |  | 17 | 2_zone |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 16 | 3_whvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 22 |  |  | 14150 | Yes |  |  |  | Setup | ON | Scan |  |  |  |  | 18 | 2_zone | 2 -> 3 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data | 17 | 3_whvent | 3 -> 4 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 23 |  |  | 14150 | Yes |  |  |  | Scan x 25 | ON | Scan |  |  |  |  | 19 | 3_whvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data | 18 | 4_fvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 24 |  |  | 14150 | Yes |  |  |  | Scan x 25 | ON | Scan |  |  |  |  | 20 | 3_whvent |  | Scan x 25 |  | 5_whvent | 5 -> 6 | ON | Yes | Use data | 19 | 4_fvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 25 |  |  | 11160 | Yes | Setup |  |  |  | ON |  | Setup |  |  |  | 21 | 3_whvent | 3 -> 4 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 20 | 4_fvent | 4 -> 1 | Scan x 25 |  | 5_whvent | 5 -> 6 | ON | Yes | Use data
| 26 |  |  | 11160 | Yes | Scan x 25 |  |  |  | ON |  | Scan |  |  |  | 22 | 4_fvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay | 21 | 1_zero |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay
| 27 |  |  | 11160 | Yes | Scan x 25 |  |  |  | ON |  | Scan |  |  |  | 23 | 4_fvent |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 22 | 1_zero |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 28 |  |  | 12160 | Yes |  | Setup |  |  | ON |  | Scan |  |  |  | 24 | 4_fvent | 4 -> 1 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 23 | 1_zero | 1 -> 2 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 29 |  |  | 12160 | Yes |  | Scan x 25 |  |  | ON |  | Scan |  |  |  | 25 | 1_zero |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay | 24 | 2_zone |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay
| 30 |  |  | 12160 | Yes |  | Scan x 25 |  |  | ON |  | Scan |  |  |  | 26 | 1_zero |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 25 | 2_zone |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 31 |  |  | 13160 | Yes |  |  | Setup |  | ON |  | Scan |  |  |  | 27 | 1_zero | 1 -> 2 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 26 | 2_zone | 2 -> 3 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 32 |  |  | 13160 | Yes |  |  | Scan x 25 |  | ON |  | Scan |  |  |  | 28 | 2_zone |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay | 27 | 3_whvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay
| 33 |  |  | 13160 | Yes |  |  | Scan x 25 |  | ON |  | Scan |  |  |  | 29 | 2_zone |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 28 | 3_whvent |  | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 34 |  |  | 14160 | Yes |  |  |  | Setup | ON |  | Scan |  |  |  | 30 | 2_zone | 2 -> 3 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay | 29 | 3_whvent | 3 -> 4 | Scan x 25 |  | 6_fvent |  | ON | Yes? | Setup delay
| 35 |  |  | 14160 | Yes |  |  |  | Scan x 25 | ON |  | Scan |  |  |  | 31 | 3_whvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data | 30 | 4_fvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes? | Setup delay
| 36 |  |  | 14160 | Yes |  |  |  | Scan x 25 | ON |  | Scan |  |  |  | 32 | 3_whvent |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 31 | 4_fvent |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 37 |  |  | 11160 | Yes | Setup |  |  |  | ON |  | Scan |  |  |  | 33 | 3_whvent | 3 -> 4 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 32 | 4_fvent | 4 -> 1 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 38 |  |  | 11160 | Yes | Scan x 25 |  |  |  | ON |  | Scan |  |  |  | 34 | 4_fvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data | 33 | 1_zero |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data
| 39 |  |  | 11160 | Yes | Scan x 25 |  |  |  | ON |  | Scan |  |  |  | 35 | 4_fvent |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 34 | 1_zero |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 40 |  |  | 12160 | Yes |  | Setup |  |  | ON |  | Scan |  |  |  | 36 | 4_fvent | 4 -> 1 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 35 | 1_zero | 1 -> 2 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 41 |  |  | 12160 | Yes |  | Scan x 25 |  |  | ON |  | Scan |  |  |  | 37 | 1_zero |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data | 36 | 2_zone |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data
| 42 |  |  | 12160 | Yes |  | Scan x 25 |  |  | ON |  | Scan |  |  |  | 38 | 1_zero |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 37 | 2_zone |  | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 43 |  |  | 13160 | Yes |  |  | Setup |  | ON |  | Scan |  |  |  | 39 | 1_zero | 1 -> 2 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data | 38 | 2_zone | 2 -> 3 | Scan x 25 |  | 6_fvent |  | ON | Yes | Use data
| 44 |  |  | 13160 | Yes |  |  | Scan x 25 |  | ON |  | Scan |  |  |  | 40 | 2_zone |  | Scan x 25 | Setup delay? | 6_fvent | 6 -> 7 | ON | Yes | Use data | 39 | 3_whvent |  | Scan x 25 | Setup delay? | 6_fvent |  | ON | Yes | Use data
| 45 |  |  | 13160 | Yes |  |  | Scan x 25 |  | ON |  | Scan |  |  |  | 41 | 2_zone |  | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 40 | 3_whvent |  | Scan x 25 |  | 6_fvent | 6 -> 7 | ON | Yes | Use data
| 46 |  |  | 14160 | Yes |  |  |  | Setup | ON |  | Scan |  |  |  | 42 | 2_zone | 2 -> 3 | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 41 | 3_whvent | 3 -> 4 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 47 |  |  | 14160 | Yes |  |  |  | Scan x 25 | ON |  | Scan |  |  |  | 43 | 3_whvent |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes? | Setup delay | 42 | 4_fvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 48 |  |  | 14160 | Yes |  |  |  | Scan x 25 | ON |  | Scan |  |  |  | 44 | 3_whvent |  | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 43 | 4_fvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 49 |  |  | 11170 | Yes | Setup |  |  |  | ON |  |  | Setup |  |  | 45 | 3_whvent | 3 -> 4 | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 44 | 4_fvent | 4 -> 1 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 50 |  |  | 11170 | Yes | Scan x 25 |  |  |  | ON |  |  | Scan |  |  | 46 | 4_fvent |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes? | Setup delay | 45 | 1_zero |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 51 |  |  | 11170 | Yes | Scan x 25 |  |  |  | ON |  |  | Scan |  |  | 47 | 4_fvent |  | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 46 | 1_zero |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 52 |  |  | 12170 | Yes |  | Setup |  |  | ON |  |  | Scan |  |  | 48 | 4_fvent | 4 -> 1 | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 47 | 1_zero | 1 -> 2 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 53 |  |  | 12170 | Yes |  | Scan x 25 |  |  | ON |  |  | Scan |  |  | 49 | 1_zero |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes? | Setup delay | 48 | 2_zone |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes? | Setup delay
| 54 |  |  | 12170 | Yes |  | Scan x 25 |  |  | ON |  |  | Scan |  |  | 50 | 1_zero |  | Scan x 25 |  | 7_room |  | ON | Yes? | Setup delay | 49 | 2_zone |  | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 55 |  |  | 13170 | Yes |  |  | Setup |  | ON |  |  | Scan |  |  | 51 | 1_zero | 1 -> 2 | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 50 | 2_zone | 2 -> 3 | Scan x 25 |  | 5_whvent |  | ON | Yes? | Setup delay
| 56 |  |  | 13170 | Yes |  |  | Scan x 25 |  | ON |  |  | Scan |  |  | 52 | 2_zone |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes | Use data | 51 | 3_whvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 57 |  |  | 13170 | Yes |  |  | Scan x 25 |  | ON |  |  | Scan |  |  | 53 | 2_zone |  | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 52 | 3_whvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 58 |  |  | 14170 | Yes |  |  |  | Setup | ON |  |  | Scan |  |  | 54 | 2_zone | 2 -> 3 | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 53 | 3_whvent | 3 -> 4 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 59 |  |  | 14170 | Yes |  |  |  | Scan x 25 | ON |  |  | Scan |  |  | 55 | 3_whvent |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes | Use data | 54 | 4_fvent |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 60 |  |  | 14170 | Yes |  |  |  | Scan x 25 | ON |  |  | Scan |  |  | 56 | 3_whvent |  | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 55 | 4_fvent |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 61 |  |  | 11170 | Yes | Setup |  |  |  | ON |  |  | Scan |  |  | 57 | 3_whvent | 3 -> 4 | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 56 | 4_fvent | 4 -> 1 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 62 |  |  | 11170 | Yes | Scan x 25 |  |  |  | ON |  |  | Scan |  |  | 58 | 4_fvent |  | Scan x 25 | Setup delay? | 7_room |  | ON | Yes | Use data | 57 | 1_zero |  | Scan x 25 | Setup delay? | 5_whvent |  | ON | Yes | Use data
| 63 |  |  | 11170 | Yes | Scan x 25 |  |  |  | ON |  |  | Scan |  |  | 59 | 4_fvent |  | Scan x 25 |  | 7_room |  | ON | Yes | Use data | 58 | 1_zero |  | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 64 |  |  | 12170 | Yes |  | Setup |  |  | ON |  |  | Scan |  |  | 60 | 4_fvent | 4 -> 1 | Scan x 25 |  | 7_room | off | off | Yes | Use data | 59 | 1_zero | 1 -> 2 | Scan x 25 |  | 5_whvent |  | ON | Yes | Use data
| 65 |  |  | 12170 | Yes |  | Scan x 25 |  |  | ON |  |  | Scan |  |  | 1 | 1_zero |  | Scan x 25 | Setup delay? | off |  | off | No | No | 60 | 2_zone |  | Scan x 25 | Setup delay? | 7_room | off | off | Yes | Use data
| 66 |  |  | 12170 | Yes |  | Scan x 25 |  |  | ON |  |  | Scan |  |  | 2 | 1_zero |  | Scan x 25 |  | off |  | off | No | No | 1 | 2_zone |  | Scan x 25 |  | off |  | off | No | No
| 67 |  |  | 13170 | Yes |  |  | Setup |  | ON |  |  | Scan |  |  | 3 | 1_zero | 1 -> 2 | Scan x 25 |  | off |  | off | No | No | 2 | 2_zone | 2 -> 3 | Scan x 25 |  | off |  | off | No | No
| 68 |  |  | 13170 | Yes |  |  | Scan x 25 |  | ON |  |  | Scan |  |  | 4 | 2_zone |  | Scan x 25 | Setup delay? | off |  | off | No | No | 3 | 3_whvent |  | Scan x 25 | Setup delay? | off |  | off | No | No
| 69 |  |  | 13170 | Yes |  |  | Scan x 25 |  | ON |  |  | Scan |  |  |  | Repeat except CO2 samplng performed only occasionally | [8 empty] | 4 | 3_whvent |  | Scan x 25 |  | off |  | off | No | No
| 70 |  |  | 14170 | Yes |  |  |  | Setup | ON |  |  | Scan
| 71 |  |  | 14170 | Yes |  |  |  | Scan x 25 | ON |  |  | Scan
| 72 |  |  | 14170 | Yes |  |  |  | Scan x 25 | ON |  |  | Scan
| 73 |  |  | 10000 | Yes |  |  |  |  | OFF
| 74 |  |  | 10000 | Yes |  |  |  |  | OFF
| 75 |  |  | 10000 | Yes |  |  |  |  | OFF
| 76 |  |  | 10000 | Yes |  |  |  |  | OFF
| 77 |  |  | 10000 | Yes |  |  |  |  | OFF
| 78 |  |  | 10000 | Yes |  |  |  |  | OFF
| 79 |  |  | 10000 | Yes |  |  |  |  | OFF
| 80 |  |  | 10000 | Yes |  |  |  |  | OFF
| 81 |  |  | 10000 | Yes |  |  |  |  | OFF
| 82 |  |  | 10000 | Yes |  |  |  |  | OFF
| 83 |  |  | 10000 | Yes |  |  |  |  | OFF
| 84 |  |  | 10000 | Yes |  |  |  |  | OFF
| 85 |  |  | 10000 | Yes |  |  |  |  | OFF
| 86 |  |  | 10000 | Yes |  |  |  |  | OFF
| 87 |  |  | 10000 | Yes |  |  |  |  | OFF
| 88 |  |  | 10000 | Yes |  |  |  |  | OFF
| 89 |  |  | 10000 | Yes |  |  |  |  | OFF
| 90 |  |  | 10000 | Yes |  |  |  |  | OFF
Note on AK12: Actually want to start on the vent of the operating appliance.

## HardwareMapping
Board label | Connector designation | Amp | ADC | ADC mux # | I2C Address | BBB pins | BBB name | Connected device | Possible data parameter name (coordinate with object names) | Notes
TC1 | J20 1-2 | U17 | U11 | 0 | x | P9-17 (I2C1_SCL) P9-18 (I2C1_SDA) | I2C1 | WH burner temp | .whburner
TC2 | J20 3-4 | U16 | U11 | 1 |  | " | " | WH spill temp 1 | .whspill_1
TC3 | J20 5-6 | U18 | U11 | 2 |  | " | " | WH spill temp 2 | .whspill_2
TC4 | J20 7-8 | U19 | U11 | 3 |  | " | " | WH spill temp 3 | .whspill_3
TC5 | J20 9-10 | U20 | U13 | 0 | x | " | I2C1 | WH spill temp 4 | .whspill_4
TC6 | J20 11-12 | U21 | U13 | 1 |  | " | " | WH downstream vent temp | .whvent
TC7 | J21 1-2 | U22 | U13 | 2 |  | " | " | Furnace burner temp | .fburner
TC8 | J21 3-4 | U23 | U13 | 3 |  | " | " | Furnace spill temp 1 | .fspill_1
TC9 | J21 5-6 | U24 | U14 | 0 | x | " | I2C1 | Furnace spill temp 2 | .fspill_2
TC10 | J21 7-8 | U25 | U14 | 1 |  | " | " | Furnace spill temp 3 | .fspill_3
TC11 | J21 9-10 | U26 | U14 | 2 |  | " | " | Furnace spill temp 4 | .fspill_4
TC12 | J21 11-12 | U27 | U14 | 3 |  | " | " | Furnace downstream vent temp | .fvent
TC13 | J10 1-2 | U28 | U15 | 0 | x | " | I2C1 | Zone high temp | .zonehi
TC14 | J10 4-5 | U29 | U15 | 1 |  | " | " | Zone low temp | .zonelow
TC15 | J10 6-7 | U30 | U15 | 2 |  | " | " | Outdoor temp | .outdoor | TC amps U30 and U31 include voltage offset to allow reading temps < 32F
| J10 9-10 | U31 | U15 | 3 |  | " | " | Not used
[5 empty] | 0x28 | " | I2C1 | Pressure DLVR | [multiple] | Multiple data parameters, tied to valve position.
[5 empty] | x | " | I2C1 | RTC
JP1-A | J9-2 | na | U8 | 0 | x | P9-19 (I2C2_SCL) P9-20 (I2C2_SDA) | I2C2 | Door position | .door_1
JP1-B | J9-4 | na | U8 | 1 |  | " | " | Fan current 1 | .fan_1
JP1-C | J9-6 | na | U8 | 2 |  | " | " | Fan current 2 | .fan_2
JP1-D | J9-8 | U3 | U8 | 3 |  | " | " | Carbon monoxide | .cozone
ADC-6 | J25-1 | na | U9 | 0 | x | " | I2C2 | Carbon dioxide | [multiple] | Can put on any U9 or U10 input. Multiple data parameters, tied to valve position.
| J25-2 | na | U9 | 1 |  | " | " | Not used
| J25-3 | na | U9 | 2 |  | " | " | Not used
| J25-4 | na | U9 | 3 |  | " | " | Battery
ADC-7 | J25-5 | na | U10 | 0 | x | " | I2C2 | Not used
| J25-6 | na | U10 | 1 |  | " | " | Not used
| J25-7 | na | U10 | 2 |  | " | " | Not used
| J25-8 | na | U10 | 3 |  | " | " | Not used
[6 empty] | P9-11 | UART4_RXD | Xbee Dout (pin 2)
[6 empty] | P9-13 | UART4_TXD | Xbee Din (pin 3)
[6 empty] | P8-7 |  | Valve 1 zero pressure
[6 empty] | P8-8 |  | Valve 2 WH vent pressure
[6 empty] | P8-9 |  | Valve 3 Furnace vent pressure
[6 empty] | P8-10 |  | Valve 4 Zone pressure
[6 empty] | P8-11 |  | Valve 5 CO2 WH
[6 empty] | P8-12 |  | Valve 6 CO2 Furnace
[6 empty] | P8-13 |  | Valve 7 CO2 Zone
[6 empty] | P8-14 |  | Pump |  | Pump must be on P8-14 since it switches 3.3 V power
[6 empty] | P8-15 |  | Controls 24V power |  | Actively switched by BBB to avoid damage to inputs
[6 empty] | P8-16 |  | Switch_1 |  | Pushbutton switch - may use to start 1-sec data collection in setup/testing
[6 empty] | P8-17 |  | Switch_2 |  | No function designated

## DataParameters
Note when multiple summary values are collected in 60-sec scan (e.g. avg, min, max), each needs to have a separate field in data record
Sensor or I/O device description | Object attribute in code (to be edited) | Parameter name (in data file header) | Value used in 1-sec records | Value used in 60-sec record | Notes
Site ID |  | site | VALUE | VALUE
Timestamp | time | time | VALUE | 1st | Use timestamp of 1st second incorporated in record
Record number |  | rec_num | VALUE | VALUE | Incremented for each record. Start from 1 on any code re-start.
WH burner temp | .whburner | t_whburner | sample | avg
|  | t_whburner_min | sample | min
|  | t_whburner_max | sample | max
WH spill temp 1 | .whspill_1 | t_whspill1 | sample | avg
|  | t_whspill1_min | sample | min
|  | t_whspill1_max | sample | max
WH spill temp 2 | .whspill_2 | t_whspill2 | sample | avg
|  | t_whspill2_min | sample | min
|  | t_whspill2_max | sample | max
WH spill temp 3 | .whspill_3 | t_whspill3 | sample | avg
|  | t_whspill3_min | sample | min
|  | t_whspill3_max | sample | max
WH spill temp 4 | .whspill_4 | t_whspill4 | sample | avg
|  | t_whspill4_min | sample | min
|  | t_whspill4 | sample | max
WH downstream vent temp | .whvent | t_whvent | sample | avg
|  | t_whvent_min | sample | min
|  | t_whvent_max | sample | max
Furnace burner temp | .fburner | t_fburner | sample | avg
|  | t_fburner_min | sample | min
|  | t_fburner_max | sample | max
Furnace spill temp 1 | .fspill_1 | t_fspill1 | sample | avg
|  | t_fspill1_min | sample | min
|  | t_fspill1_max | sample | max
Furnace spill temp 2 | .fspill_2 | t_fspill2 | sample | avg
|  | t_fspill2_min | sample | min
|  | t_fspill2_max | sample | max
Furnace spill temp 3 | .fspill_3 | t_fspill3 | sample | avg
|  | t_fspill3_min | sample | min
|  | t_fspill3_max | sample | max
Furnace spill temp 4 | .fspill_4 | t_fspill4 | sample | avg
|  | t_fspill4_min | sample | min
|  | t_fspill4_max | sample | max
Furnace downstream vent temp | .fvent | t_fvent | sample | avg
|  | t_fvent_min | sample | min
|  | t_fvent_max | sample | max
Zone high temp | .zonehi | t_zonehi | sample | avg
|  | t_zonehi_min | sample | min
|  | t_zonehi_max | sample | max
Zone low temp | .zonelow | t_zonelow | sample | avg
|  | t_zonelow_min | sample | min
|  | t_zonelow_max | sample | max
Outdoor temp | .outdoor | t_outdoor | sample | avg
|  | t_outdoor_min | sample | min
|  | t_outdoor_max | sample | max
Place holder for extra temp |  | t_extra | sample | avg | These are placeholders for a possible added temperature
|  | t_extra_min | sample | min
|  | t_extra_max | sample | max
Door position | .door_1 | pos_door1 | sample | avg
|  | pos_door1_min | sample | min
|  | pos_door1_max | sample | max
Fan current 1 | .fan_1 | i_fan1 | sample | avg
|  | i_fan1_min | sample | min
|  | i_fan1_max | sample | max
Fan current 2 | .fan_2 | i_fan2 | sample | avg
|  | i_fan2_min | sample | min
|  | i_fan2_max | sample | max
Carbon monoxide | .cozone | ppm_co | sample | avg
|  | ppm_co_min | sample | min
|  | ppm_co_max | sample | max
CO2 location (valve) ID |  | loc_co2 | VALUE | Last value? | Capture 1st or last valve ID in 60-sec record. Record values by location ID, i.e. put each measurement in a separate parameter (see next few lines). Recording current ID in detailed data collection is a check on this.
CO2 valve time on |  | sec_co2 | VALUE | Last value? | Number of seconds the current valve has been open - use to screen out data before settling time has passed
CO2 WH vent | .wh | ppm_co2_whvent | sample | avg | Record always in 1-sec data collection, use if current (i.e. settling time has passed) in 60-sec record periods.
|  | ppm_co2_whvent_min | sample | min | Same as above
|  | ppm_co2_whvent_max | sample | max | Same as above
CO2 F vent | .f | ppm_co2_fvent | sample | avg | Same as above
|  | ppm_co2_fvent_min | sample | min | Same as above
|  | ppm_co2_fvent_max | sample | max | Same as above
CO2 Zone | .zone | ppm_co2_zone | sample | avg | Same as above
|  | ppm_co2_zone_min | sample | min | Same as above
|  | ppm_co2_zone_max | sample | max | Same as above
Pressure location (valve) ID |  | loc_p | VALUE | Last value? | Record values by location ID, i.e. put each pressure measurement in a separate parameter (see next few lines). Recording current ID in detailed data collection is a check on this.
Pressure valve time on |  | sec_p | VALUE | Last value? | Number of seconds the valve has been open - use to screen out data before settling time has passed
Pressure zero - avg in scan | .zero | p_zero | sample | avg | Record always in 1-sec data collection, use if current (i.e. settling time has passed) in 60-sec record periods. Average value within each scan.
|  | p_zero_min | sample | min
|  | p_zero_max | sample | max
Pressure zero - range in scan | .zerorange | p_zero_rng | sample | avg | Range is max - min within a 1-sec scan. May use std dev instead of range for 60-sec records.
|  | p_zero_rng_min | sample | min
|  | p_zero_rng_max | sample | max
Pressure wh vent - avg in scan | .whvent | p_whvent | sample | avg | Subtract current zero offset
|  | p_whvent_min | sample | min
|  | p_whvent_max | sample | max
Pressure wh vent - range in scan | .whventrange | p_whvent_rng | sample | avg | Range is max - min within a 1-sec scan. May use std dev instead of range for 60-sec records.
|  | p_whvent_rng_min | sample | min
|  | p_whvent_rng_max | sample | max
Pressure f vent - avg in scan | .fvent | p_fvent | sample | avg | Subtract current zero offset
|  | p_fvent_min | sample | min
|  | p_fvent_max | sample | max
Pressure f vent - range in scan | .fventrange | p_fvent_rng | sample | avg | Range is max - min within a 1-sec scan. May use std dev instead of range for 60-sec records.
|  | p_fvent_rng_min | sample | min
|  | p_fvent_rng_max | sample | max
Pressure zone - avg in scan | .zone | p_zone | sample | avg | Subtract current zero offset
|  | p_zone_min | sample | min
|  | p_zone_max | sample | max
Pressure zone - range in scan | .zonerange | p_zone_rng | sample | avg | Range is max - min within a 1-sec scan. May use std dev instead of range for 60-sec records.
|  | p_zone_rng_min | sample | min
|  | p_zone_rng_max | sample | max
wh burner status |  | wh_status | VALUE | Last | In 60-sec records, use value from last scan
wh mode |  | wh_mode | VALUE | Last | Mode during last second of data included in record
f burner status |  | f_status | VALUE | Last
f mode |  | f_mode | VALUE | Last
system state |  | sys_state | VALUE | VALUE
number_of_scans |  | scans_accum | COUNT | COUNT | Number of scans represented in record (usually 1 or 60). Take this from t_outdoor, or any value that should be present in every scan.
wh burner run time from burner start | time.whburnerrun | sec_whrun | VALUE | Max | Seconds of operation from burner start. In 60-sec record, should always evaluate to zero.
f burner run time from burner start | time.fburnerrun | sec_frun | VALUE | Max | Seconds of operation from burner start. In 60-sec record, should always evaluate to zero.
wh cooldown time |  | sec_whcooldown | VALUE | Max | Seconds of cooldown from burner stop. Set to 0 when in system state 5 or 6.
f cooldown time |  | sec_fcooldown | VALUE | Max | Seconds of cooldown from burner stop. Set to 0 when in system state 5 or 6.
Count of 1-second values in record |  | sec_count | COUNT | COUNT | This is the divisor use to calculate averages over the record period. Should always evaluate to 1 in 1-sec records.
Number of Xbee1 values |  | n_xbee1 | COUNT | COUNT
Xbee 1 current (i) as voltage |  | vi_xbee1 | sample | avg | Any Xbee may be set up to measure current, pressure, or door position. The configuration file will determine what type of data is present
Xbee 1 pressure (p) as voltage |  | vp_xbee1 | sample | avg
Xbee 1 door position (pos) as voltage |  | vpos_xbee1 | sample | avg
Xbee 1 battery voltage |  | vbatt_xbee1 | sample | avg
Number of Xbee2 values |  | n_xbee2 | COUNT | COUNT
Xbee 2 current (i) as voltage |  | vi_xbee2 | sample | avg | Allow for up to 3 Xbees: A, B, C
Xbee 2 pressure (p) as voltage |  | vp_xbee2 | sample | avg
Xbee 2 door position (pos) as voltage |  | vpos_xbee2 | sample | avg | Add Xbee min & max values?
Xbee 2 battery voltage |  | vbatt_xbee2 | sample | avg
Number of Xbee3 values |  | n_xbee3 | COUNT | COUNT
Xbee 3 current (i) as voltage |  | vi_xbee3 | sample | avg
Xbee 3 pressure (p) as voltage |  | vp_xbee3 | sample | avg
Xbee 3 door position (pos) as voltage |  | vpos_xbee3 | sample | avg
Xbee 3 battery voltage |  | vbatt_xbee3 | sample | avg
Data file MB/day | 3.024
Parameters | 150
Avg char per parameter | 7
Avg records per minute | 20

## DiagnosticsData
DIAGNOSTICS
Sensor or I/O device description | Name (coordinate with object names) | Parameter name (base) | Parameter name (typ min) | Parameter name (typ max) | Value in diagnostics record | Minimum _min | Maximum _max | Count _cnt | Other | Notes
Accumulated pump run time (hrs)
errors |  |  |  |  | Sum? |  |  | x | Sum? | Sum of binary bit error values set in wh and furnace mode routines. Don't expect multiple errors to occur duinrg 60-sec record periods.